## Sheet1
Item Class | Function | Maintainable Item | Maintainable Item Function | Symptom | Failure Mechanism | Failure Effect | Treatment Actions | Reporting Question ID | Treatment Action Type
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | ELP - External leakage - process medium | 2.2 Corrosion | Corrosion perforation causes process fluid leak to environment | Plate thickness UT measurement [Y/N]; Visual pitting inspection [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | ELP - External leakage - process medium | 2.6 Fatigue | Fatigue crack through plate allows process fluid escape | Eddy current crack detection [Y/N]; Pressure test [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | ELP - External leakage - process medium | 2.3 Erosion | Erosive wear at inlet zone perforates plate | Plate thickness inspection at inlet zones [Y/N]; Flow velocity check [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | ELP - External leakage - process medium | 2.5 Breakage | Catastrophic plate rupture releases large volume of process fluid | Emergency shutdown valve test [Y/N]; Burst disk inspection [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | ILP - Internal leakage - process medium | 2.2 Corrosion | Corrosion creates leak path between hot and cold fluid channels | Pressure decay test between circuits [Y/N]; Cross-contamination fluid analysis [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | ILP - Internal leakage - process medium | 2.6 Fatigue | Fatigue crack joins adjacent flow channels | Dye penetration test on plates [Y/N]; Fatigue cycle tracking [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | ILP - Internal leakage - process medium | 2.4 Wear | Gasket groove wear creates bypass path between streams | Plate gasket groove condition inspection [Y/N]; Surface profile measurement [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | ILP - Internal leakage - process medium | 2.1 Cavitation | Cavitation damage erodes plate material causing cross-flow | Inlet pressure monitoring for cavitation margin [Y/N]; Plate inlet zone inspection [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | PDE - Parameter deviation | 5.2 Contamination | Fouling on plate surfaces reduces heat transfer efficiency | Online differential pressure monitoring [Y/N]; Plate cleaning performed per schedule [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | PDE - Parameter deviation | 5.1 Blockage/plugged | Partial channel blockage causes flow and temperature deviation | Plate channel inspection for fouling [Y/N]; Backflushing verification [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | PDE - Parameter deviation | 2.2 Corrosion | Surface roughness from corrosion changes flow characteristics | Corrosion coupon monitoring [Y/N]; pH and chemistry analysis [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | PDE - Parameter deviation | 1.4 Deformation | Plate distortion alters flow distribution between channels | Plate flatness inspection during maintenance [Y/N]; Compression gap measurement [Y/N] | TBD | Preventive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | IHT - Insufficient heat transfer | 5.2 Contamination | Fouling layer reduces thermal conductivity between streams | Thermal performance calculation against design [Y/N]; Cleaning frequency review [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | IHT - Insufficient heat transfer | 5.1 Blockage/plugged | Channel blockage reduces effective heat transfer area | Flow distribution check across plate pack [Y/N]; Plate channel inspection [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | IHT - Insufficient heat transfer | 1.4 Deformation | Plate warping reduces contact area between fluid streams | Plate straightness verification [Y/N]; Replacement criteria check [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | IHT - Insufficient heat transfer | 2.2 Corrosion | Corrosion product scaling insulates plate surface | Water/fluid chemistry analysis [Y/N]; Descaling schedule verification [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | PLU - Plugged/choked | 5.2 Contamination | Debris and fouling completely block plate channels | Inline filter condition check upstream [Y/N]; Chemical cleaning cycle effectiveness [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | PLU - Plugged/choked | 2.2 Corrosion | Corrosion debris obstructs flow passages | Fluid chemistry analysis [Y/N]; Debris trap inspection [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | PLU - Plugged/choked | 5.3 Miscellaneous external influences | Foreign objects entered system blocking channels | Inlet strainer condition check [Y/N]; Foreign object investigation during maintenance [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | STD - Structural deficiency | 2.2 Corrosion | Widespread corrosion reduces plate structural integrity | Ultrasonic thickness mapping of plates [Y/N]; Corrosion rate trend analysis [Y/N] | TBD | Predictive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | STD - Structural deficiency | 2.6 Fatigue | Fatigue cracking compromises plate strength | Eddy current scan for crack detection [Y/N]; Fatigue life tracking [Y/N] | TBD | Predictive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | STD - Structural deficiency | 1.4 Deformation | Thermal stress causes permanent plate warping | Plate flatness and alignment check [Y/N]; Temperature cycling monitoring [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Plates Failure | Contains and separates process fluids while providing heat transfer surface | STD - Structural deficiency | 2.5 Breakage | Plate fracture from overpressure or mechanical damage | Visual inspection for cracks/breaks [Y/N]; Pressure cycle count monitoring [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | ELP - External leakage - process medium | 2.4 Wear | Gasket material worn thin causing external process leak | Gasket compression check [Y/N]; Visual leakage inspection [Y/N] | TBD | Preventive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | ELP - External leakage - process medium | 1.4 Deformation | Gasket extrusion from overtightening causes leak path | Bolt torque verification against spec [Y/N]; Gasket replacement interval [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | ELP - External leakage - process medium | 2.2 Corrosion | Chemical attack degrades gasket material causing leakage | Gasket material compatibility check [Y/N]; Process fluid chemistry monitoring [Y/N] | TBD | Preventive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | ELP - External leakage - process medium | 2.6 Fatigue | Thermal cycling embrittles gasket causing cracking | Thermal cycle count tracking [Y/N]; Gasket hardness test [Y/N] | TBD | Predictive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | ILP - Internal leakage - process medium | 2.4 Wear | Gasket channel wear allows fluid bypass between streams | Pressure test across plate pack [Y/N]; Cross-contamination analysis [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | ILP - Internal leakage - process medium | 1.4 Deformation | Gasket misalignment or extrusion creates internal bypass | Gasket position verification during reassembly [Y/N]; Compression gap uniformity check [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | ILP - Internal leakage - process medium | 2.6 Fatigue | Gasket fatigue cracking causes internal cross-flow | Gasket age/condition assessment [Y/N]; Replacement schedule compliance [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | ILP - Internal leakage - process medium | 2.2 Corrosion | Chemical degradation allows internal leak between channels | Process fluid chemistry check [Y/N]; Gasket material upgrade evaluation [Y/N] | TBD | Predictive; Redesign
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | PDE - Parameter deviation | 2.4 Wear | Gradual gasket degradation changes flow parameters | Differential pressure trend monitoring [Y/N]; Gasket condition assessment during PM [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | PDE - Parameter deviation | 1.3 Clearance/alignment failure | Incorrect plate compression allows gasket movement | Compression gap measurement [Y/N]; Plate pack alignment check [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | PDE - Parameter deviation | 5.3 Miscellaneous external influences | Foreign object damage during assembly causes gasket defect | Installation procedure verification [Y/N]; Foreign object inspection during reassembly [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | IHT - Insufficient heat transfer | 2.4 Wear | Worn gaskets cause fluid bypass reducing thermal performance | Thermal performance trending [Y/N]; Gasket replacement schedule check [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | IHT - Insufficient heat transfer | 1.4 Deformation | Gasket extrusion causes fluid short-circuiting between channels | Plate pack compression check [Y/N]; Gasket groove condition inspection [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | STD - Structural deficiency | 2.5 Breakage | Gasket rupture leads to uncontrolled leakage | Visual inspection for gasket damage [Y/N]; Gasket service life tracking [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | STD - Structural deficiency | 2.6 Fatigue | Gasket embrittlement and cracking from age | Gasket flexibility test [Y/N]; Replacement based on operating hours [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | STD - Structural deficiency | 2.2 Corrosion | Chemical degradation destroys gasket structure | Elastomer compatibility test with process fluid [Y/N]; NACE standard compliance check [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Gasket Seals Failure * | Provides leak-tight sealing between plates to prevent fluid mixing and external leakage | STD - Structural deficiency | 2.4 Wear | Gasket material thinning reduces sealing structural integrity | Gasket thickness measurement [Y/N]; Wear limit verification [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | STD - Structural deficiency | 2.2 Corrosion | Frame corrosion weakens structural capacity | Frame coating integrity inspection [Y/N]; Frame thickness measurement [Y/N] | TBD | Predictive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | STD - Structural deficiency | 2.6 Fatigue | Frame cracking reduces clamping force on plates | Frame weld NDT inspection [Y/N]; Structural integrity assessment [Y/N] | TBD | Predictive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | STD - Structural deficiency | 1.4 Deformation | Frame warping causes uneven plate compression | Frame alignment and parallelism measurement [Y/N]; Foundation settlement check [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | STD - Structural deficiency | 2.5 Breakage | Frame bar or tie bolt fracture | Visual inspection of frame members [Y/N]; Tie bolt condition check [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | ELP - External leakage - process medium | 2.2 Corrosion | Frame corrosion allows process fluid to bypass gaskets | Corrosion mapping of frame components [Y/N]; Leak detection survey [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | ELP - External leakage - process medium | 1.4 Deformation | Frame distortion causes gasket seal failure | Frame flatness measurement [Y/N]; Tie bolt torque verification [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | ELP - External leakage - process medium | 2.6 Fatigue | Frame crack allows fluid passage to atmosphere | NDT of frame bolts and structure [Y/N]; Crack propagation monitoring [Y/N] | TBD | Predictive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | PDE - Parameter deviation | 1.5 Looseness | Frame bolts loosening reduces plate compression | Tie bolt torque verification [Y/N]; Slackening indicator inspection [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | PDE - Parameter deviation | 1.4 Deformation | Frame deflection causes uneven plate loading | Frame deflection measurement [Y/N]; Compression gap uniformity check [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | PDE - Parameter deviation | 1.3 Clearance/alignment failure | Misalignment between frame components | Guide bar condition check [Y/N]; Frame alignment verification [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | IHT - Insufficient heat transfer | 1.5 Looseness | Reduced plate compression allows internal fluid bypass | Compression gap check [Y/N]; Bolt re-torquing at defined interval [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | IHT - Insufficient heat transfer | 1.4 Deformation | Uneven plate compression reduces effective heat transfer | Plate pack thickness measurement [Y/N]; Thermal scanning of frame surface [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | NOI - Noise | 1.5 Looseness | Loose frame components cause rattling during operation | Frame bolt tightness check [Y/N]; Vibration monitoring [Y/N] | TBD | Preventive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | NOI - Noise | 2.2 Corrosion | Corroded surfaces cause fretting noise between components | Frame cleaning and coating renewal [Y/N]; Guide bar lubrication check [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | VIB - Vibration | 1.5 Looseness | Loose frame bolts causing structural vibration | Bolt torque check [Y/N]; Vibration analysis [Y/N] | TBD | Preventive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | VIB - Vibration | 1.4 Deformation | Distorted frame amplifies flow-induced vibration | Frame geometry check [Y/N]; Support structure stiffness verification [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Frame Failure * | Provides structural containment and compression for the plate pack | VIB - Vibration | 2.6 Fatigue | Flow-induced vibration fatigue weakens frame | Vibration monitoring for trend analysis [Y/N]; Structural damping evaluation [Y/N] | TBD | Predictive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Nozzle/Flange Connection Failure * | Provides fluid inlet/outlet connections to the heat exchanger | ELP - External leakage - process medium | 2.2 Corrosion | Corrosion at nozzle or flange causes process fluid leak | Nozzle wall thickness UT measurement [Y/N]; Flange face corrosion inspection [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Nozzle/Flange Connection Failure * | Provides fluid inlet/outlet connections to the heat exchanger | ELP - External leakage - process medium | 2.6 Fatigue | Fatigue crack at nozzle-to-tube weld | Nozzle weld NDT inspection [Y/N]; Stress analysis review [Y/N] | TBD | Predictive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Nozzle/Flange Connection Failure * | Provides fluid inlet/outlet connections to the heat exchanger | ELP - External leakage - process medium | 1.4 Deformation | Flange gasket deformation or bolt relaxation | Flange bolt torque check [Y/N]; Gasket condition assessment [Y/N] | TBD | Preventive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Nozzle/Flange Connection Failure * | Provides fluid inlet/outlet connections to the heat exchanger | ELP - External leakage - process medium | 2.3 Erosion | High velocity flow erodes nozzle internal surface | Erosion monitoring at nozzle bends [Y/N]; Flow velocity verification [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Nozzle/Flange Connection Failure * | Provides fluid inlet/outlet connections to the heat exchanger | PDE - Parameter deviation | 1.3 Clearance/alignment failure | Nozzle misalignment causes flow restriction | Piping stress check on nozzle [Y/N]; Alignment verification [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Nozzle/Flange Connection Failure * | Provides fluid inlet/outlet connections to the heat exchanger | PDE - Parameter deviation | 5.2 Contamination | Deposit buildup inside nozzle bore restricts flow | Nozzle cleaning verification [Y/N]; Online flushing check [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Nozzle/Flange Connection Failure * | Provides fluid inlet/outlet connections to the heat exchanger | PDE - Parameter deviation | 5.3 Miscellaneous external influences | Foreign object partially blocking nozzle | Nozzle screen/strainer condition check [Y/N]; Nozzle bore inspection [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Nozzle/Flange Connection Failure * | Provides fluid inlet/outlet connections to the heat exchanger | STD - Structural deficiency | 2.2 Corrosion | Nozzle wall thinning from corrosion | Thickness measurement program [Y/N]; Corrosion rate monitoring [Y/N] | TBD | Predictive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Nozzle/Flange Connection Failure * | Provides fluid inlet/outlet connections to the heat exchanger | STD - Structural deficiency | 2.5 Breakage | Nozzle fracture from mechanical overload | Visual inspection for cracks [Y/N]; NDT of nozzle welds [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Nozzle/Flange Connection Failure * | Provides fluid inlet/outlet connections to the heat exchanger | STD - Structural deficiency | 2.6 Fatigue | Fatigue crack propagation at nozzle weld | Weld toe inspection [Y/N]; Cyclic loading monitoring [Y/N] | TBD | Predictive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Nozzle/Flange Connection Failure * | Provides fluid inlet/outlet connections to the heat exchanger | IHT - Insufficient heat transfer | 1.3 Clearance/alignment failure | Misaligned nozzle causes partial flow bypass | Flow distribution verification [Y/N]; Nozzle alignment check [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Nozzle/Flange Connection Failure * | Provides fluid inlet/outlet connections to the heat exchanger | IHT - Insufficient heat transfer | 5.2 Contamination | Nozzle bore deposits restrict flow reducing heat transfer | Nozzle pressure drop measurement [Y/N]; Differential pressure trend monitoring [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Nozzle/Flange Connection Failure * | Provides fluid inlet/outlet connections to the heat exchanger | PLU - Plugged/choked | 5.2 Contamination | Debris accumulation at nozzle restricts flow | Inlet strainer condition check [Y/N]; Nozzle bore flushing [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Nozzle/Flange Connection Failure * | Provides fluid inlet/outlet connections to the heat exchanger | PLU - Plugged/choked | 2.2 Corrosion | Corrosion products build up inside nozzle bore | Fluid chemistry analysis [Y/N]; Debris inspection [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Nozzle/Flange Connection Failure * | Provides fluid inlet/outlet connections to the heat exchanger | PLU - Plugged/choked | 5.3 Miscellaneous external influences | Foreign object full blockage of nozzle | Nozzle bore physical inspection [Y/N]; Strainer/inline filter health check [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Support Structure Failure (*) * | Provides mechanical support and maintains alignment with connected piping | STD - Structural deficiency | 2.2 Corrosion | Support corrosion weakening risks equipment settlement | Support coating integrity inspection [Y/N]; Structure thickness measurement [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Support Structure Failure (*) * | Provides mechanical support and maintains alignment with connected piping | STD - Structural deficiency | 2.6 Fatigue | Support fatigue cracking at welded joints | Weld NDT inspection [Y/N]; Structural integrity assessment [Y/N] | TBD | Predictive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Support Structure Failure (*) * | Provides mechanical support and maintains alignment with connected piping | STD - Structural deficiency | 1.4 Deformation | Support yielding under equipment weight | Level and alignment check [Y/N]; Foundation settlement monitoring [Y/N] | TBD | Preventive; Predictive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Support Structure Failure (*) * | Provides mechanical support and maintains alignment with connected piping | STD - Structural deficiency | 2.5 Breakage | Support member fracture risks equipment collapse | Visual inspection for cracks/breaks [Y/N]; Support connection bolt check [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Support Structure Failure (*) * | Provides mechanical support and maintains alignment with connected piping | PDE - Parameter deviation | 1.5 Looseness | Loose anchor bolts cause equipment misalignment | Anchor bolt torque check [Y/N]; Foundation bolt condition inspection [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Support Structure Failure (*) * | Provides mechanical support and maintains alignment with connected piping | PDE - Parameter deviation | 1.4 Deformation | Support settlement induces nozzle stress | Foundation inspection for settlement [Y/N]; Level measurement verification [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Support Structure Failure (*) * | Provides mechanical support and maintains alignment with connected piping | PDE - Parameter deviation | 1.3 Clearance/alignment failure | Support misalignment induces piping stress at nozzle | Piping stress analysis verification [Y/N]; Support adjustment check [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Support Structure Failure (*) * | Provides mechanical support and maintains alignment with connected piping | VIB - Vibration | 1.5 Looseness | Loose structural connections cause vibration | Bolt and anchor check [Y/N]; Structural tightness verification [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Support Structure Failure (*) * | Provides mechanical support and maintains alignment with connected piping | VIB - Vibration | 1.4 Deformation | Support deflection amplifies equipment vibration | Foundation settlement check [Y/N]; Support level verification [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Support Structure Failure (*) * | Provides mechanical support and maintains alignment with connected piping | VIB - Vibration | 2.6 Fatigue | Vibration-induced fatigue accelerates support degradation | Vibration monitoring [Y/N]; Support damping inspection [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Support Structure Failure (*) * | Provides mechanical support and maintains alignment with connected piping | ELP - External leakage - process medium | 1.4 Deformation | Support deflection causes excessive nozzle stress leading to flange leak | Piping stress analysis verification [Y/N]; Nozzle alignment check [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Support Structure Failure (*) * | Provides mechanical support and maintains alignment with connected piping | ELP - External leakage - process medium | 2.2 Corrosion | Support corrosion affects nozzle load distribution | Support coating renewal [Y/N]; Nozzle load calculation verification [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Support Structure Failure (*) * | Provides mechanical support and maintains alignment with connected piping | NOI - Noise | 1.5 Looseness | Loose support components rattle during operation | Support connection check [Y/N]; Shim/tightening inspection [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Support Structure Failure (*) * | Provides mechanical support and maintains alignment with connected piping | NOI - Noise | 5.3 Miscellaneous external influences | Foreign object vibration against support structure | Area cleanliness check [Y/N]; Debris removal [Y/N] | TBD | Preventive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Temperature Sensor Failure (*) | Measures fluid temperature for process control and monitoring | AIR - Abnormal instrument reading | 3.4 Out of adjustment | Temperature reading drift; calibration error | Temperature sensor calibration verification [Y/N]; Comparison with reference sensor [Y/N] | TBD | Predictive; Preventive
Heat Exchanger, Plate | Transfer heat between two fluid streams using plate and frame technology | Temperature Sensor Failure (*) | Measures fluid temperature for process control and monitoring | AIR - Abnormal instrument reading | 3.3 Faulty signal/indication/alarm | Erratic temperature signal due to sensor degradation | Sensor resistance check [Y/N]; Loop integrity test [Y/N] | TBD | Predictive; Preventive
Heat Exchanger |  | nan *