## Sheet1
Item Class | Function | Maintainable Item | Maintainable Item Function | Symptom | Failure Mechanism | Failure Effect | Treatment Actions | Reporting Question ID | Treatment Action Type
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | PDE - Parameter deviation | 2.4 Wear | Worn impeller or diffuser reduces pump discharge pressure below design specification | Pump discharge pressure at design specification? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | PDE - Parameter deviation | 2.2 Corrosion | Internal casing corrosion degrades hydraulic efficiency, reducing pressure output | Pump casing thickness verified by NDT? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | PDE - Parameter deviation | 2.3 Erosion | Erosive wear of impeller vanes reduces head capacity | Impeller condition verified during overhaul? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | VIB - Vibration | 1.3 Clearance/alignment failure | Pump-to-motor shaft misalignment induces excessive vibration | Pump/motor alignment verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | VIB - Vibration | 2.6 Fatigue | Shaft fatigue cracking generates vibration | Vibration analysis performed? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | VIB - Vibration | 1.5 Looseness | Loose foundation bolts allow pump movement generating vibration | Foundation bolts torque checked? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | NOI - Noise | 2.1 Cavitation | Cavitation bubbles collapse causing noise and impeller pitting | Pump suction pressure above NPSHR? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | NOI - Noise | 2.4 Wear | Worn bearing rolling elements generate abnormal noise | Bearing acoustic analysis normal? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | NOI - Noise | 2.6 Fatigue | Fatigue in coupling components creates abnormal sound | Coupling condition verified during inspection? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | OHE - Overheating | 1.6 Sticking | Bearing seizure from inadequate lubrication generates heat | Bearing lubricant level and condition verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | OHE - Overheating | 2.4 Wear | Worn mechanical seal face generates friction heat | Mechanical seal temperature within limits? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | OHE - Overheating | 5.1 Blockage/plugged | Recirculation path blockage causes internal heat buildup in pump casing | Pump casing temperature monitored? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | ELP - External leakage - process medium | 2.2 Corrosion | Casing corrosion pit penetrates wall causing water loss | Pump casing free of active corrosion? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | ELP - External leakage - process medium | 1.4 Deformation | Gasket compression set causes flange joint water leak | Flange bolts torque and gasket condition verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | LOO - Low output | 2.3 Erosion | Eroded impeller reduces pump flow capacity | Pump flow rate measured at design RPM? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | LOO - Low output | 2.4 Wear | Worn wear rings increase internal recirculation reducing net output | Pump internal clearances verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Water Mist Pump Failure * | Pressurize water from reservoir into the distribution piping network at required flow and pressure for mist generation | LOO - Low output | 5.1 Blockage/plugged | Suction strainer partial blockage restricts inlet flow to pump | Suction strainer clean and unobstructed? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | ELP - External leakage - process medium | 2.2 Corrosion | Corrosion pinhole in pipe wall causes water spray loss | Piping thickness verified by UT inspection? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | ELP - External leakage - process medium | 2.6 Fatigue | Fatigue crack at weld joint causes water leak | Weld inspection performed by MPI? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | ELP - External leakage - process medium | 1.4 Deformation | Mechanical impact damage deforms pipe creating leak path | Piping free of mechanical damage? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | STD - Structural deficiency | 2.2 Corrosion | Generalized wall thinning reduces pipe pressure rating below system demand | Pipe wall thickness minimum verified by NDT? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | STD - Structural deficiency | 1.4 Deformation | Pipe support corrosion causes sagging and excessive stress on pipe joints | Pipe supports condition verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | STD - Structural deficiency | 2.5 Breakage | Freeze damage causes pipe rupture in exposed sections | Piping heat tracing functional where installed? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | PLU - Plugged/choked | 5.2 Contamination | Debris accumulation from construction debris blocks pipe cross-section | Piping flushed and clear after installation/modification? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | PLU - Plugged/choked | 2.2 Corrosion | Corrosion scale buildup restricts internal diameter | Piping internal condition verified by scope? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | PDE - Parameter deviation | 2.2 Corrosion | Internal corrosion roughness increases friction loss, reducing downstream pressure | Flow test results compare to baseline? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | PDE - Parameter deviation | 5.2 Contamination | Partial debris obstruction causes section pressure deviation from design | Section pressure gauges reading within expected range? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | PDE - Parameter deviation | 1.3 Clearance/alignment failure | Pipe support failure alters routing causing flow restriction | Pipe support alignment verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | VIB - Vibration | 1.5 Looseness | Loose pipe clamps allow pipe movement during flow | Pipe clamps secure and tight? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | VIB - Vibration | 2.6 Fatigue | Water hammer fatigue causes pipe movement and vibration | Surge suppression devices functional? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | VIB - Vibration | 5.3 Miscellaneous external influences | Adjacent equipment vibration transmitted to piping system | Pipe vibration dampers condition verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | BRD - Breakdown | 2.5 Breakage | Catastrophic pipe rupture from overpressure event | PRD tested and functional? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Piping System Failure * | Transport pressurized water from pump station to all nozzle arrays throughout the protected area | BRD - Breakdown | 2.6 Fatigue | Fatigue failure from repeated pressure surges | System pressure surge cycles recorded? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Nozzle Failure | Discharge pressurized water as fine mist droplets for effective fire suppression by cooling and oxygen displacement | PLU - Plugged/choked | 5.2 Contamination | Sediment or debris lodges in nozzle orifice blocking flow | Nozzle flushed and free of debris? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Nozzle Failure | Discharge pressurized water as fine mist droplets for effective fire suppression by cooling and oxygen displacement | PLU - Plugged/choked | 2.2 Corrosion | Corrosion scale breaks loose from pipe interior and blocks nozzle opening | Nozzle internal passage clear of scale? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Nozzle Failure | Discharge pressurized water as fine mist droplets for effective fire suppression by cooling and oxygen displacement | PLU - Plugged/choked | 2.3 Erosion | Erosion debris from pipe interior lodges inside nozzle | Downstream strainer effective at protecting nozzles? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Nozzle Failure | Discharge pressurized water as fine mist droplets for effective fire suppression by cooling and oxygen displacement | PDE - Parameter deviation | 2.4 Wear | Orifice wear changes spray droplet size distribution affecting suppression efficiency | Spray pattern tested per design specification? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Nozzle Failure | Discharge pressurized water as fine mist droplets for effective fire suppression by cooling and oxygen displacement | PDE - Parameter deviation | 2.3 Erosion | Erosion enlarges nozzle orifice reducing mist quality and coverage area | Nozzle flow rate within acceptable limits? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Nozzle Failure | Discharge pressurized water as fine mist droplets for effective fire suppression by cooling and oxygen displacement | PDE - Parameter deviation | 2.2 Corrosion | Corrosion roughens internal surface altering spray pattern | Nozzle internal condition verified by inspection? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Nozzle Failure | Discharge pressurized water as fine mist droplets for effective fire suppression by cooling and oxygen displacement | STD - Structural deficiency | 2.2 Corrosion | Nozzle body corrosion weakens structural integrity under system pressure | Nozzle body free of corrosion? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Nozzle Failure | Discharge pressurized water as fine mist droplets for effective fire suppression by cooling and oxygen displacement | STD - Structural deficiency | 1.4 Deformation | Mechanical impact deforms nozzle body | Nozzle body free of dents/damage? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Nozzle Failure | Discharge pressurized water as fine mist droplets for effective fire suppression by cooling and oxygen displacement | STD - Structural deficiency | 2.5 Breakage | Thread breakage at nozzle mounting connection | Nozzle securely attached to piping? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Nozzle Failure | Discharge pressurized water as fine mist droplets for effective fire suppression by cooling and oxygen displacement | ELP - External leakage - process medium | 1.5 Looseness | Loose nozzle-to-pipe connection leaks water | Nozzle connection tightness verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Nozzle Failure | Discharge pressurized water as fine mist droplets for effective fire suppression by cooling and oxygen displacement | ELP - External leakage - process medium | 2.2 Corrosion | Thread corrosion degrades seal causing leak at nozzle joint | Nozzle thread condition verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Nozzle Failure | Discharge pressurized water as fine mist droplets for effective fire suppression by cooling and oxygen displacement | NOI - Noise | 2.3 Erosion | Eroded orifice produces altered spray sound during operation | Nozzle operation verified by function test? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Nozzle Failure | Discharge pressurized water as fine mist droplets for effective fire suppression by cooling and oxygen displacement | NOI - Noise | 2.1 Cavitation | Cavitation at nozzle orifice creates abnormal spray noise | System pressure at nozzle within design range? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Nozzle Failure | Discharge pressurized water as fine mist droplets for effective fire suppression by cooling and oxygen displacement | NOI - Noise | 2.6 Fatigue | Fatigue crack in nozzle body creates whistling sound | Nozzle body condition verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Valve Failure | Isolate water mist system sections for maintenance, testing, and controlled water release | FTO - Failure to open on demand | 1.6 Sticking | Valve stem corrosion prevents rotation to open position | Valve stem lubricated and free moving? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Valve Failure | Isolate water mist system sections for maintenance, testing, and controlled water release | FTO - Failure to open on demand | 5.2 Contamination | Debris jammed in valve seat prevents gate movement | Valve full stroke cycle tested? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Valve Failure | Isolate water mist system sections for maintenance, testing, and controlled water release | FTO - Failure to open on demand | 2.2 Corrosion | Internal corrosion binds valve operating mechanism | Valve actuator connection free of corrosion? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Valve Failure | Isolate water mist system sections for maintenance, testing, and controlled water release | FTC - Failure to close on demand | 2.4 Wear | Worn valve seat prevents tight seal when closed | Valve seat condition verified during maintenance? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Valve Failure | Isolate water mist system sections for maintenance, testing, and controlled water release | FTC - Failure to close on demand | 1.6 Sticking | Scale buildup on guide surface prevents full closure | Valve internal surfaces cleaned? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Valve Failure | Isolate water mist system sections for maintenance, testing, and controlled water release | FTC - Failure to close on demand | 1.4 Deformation | Distorted valve gate prevents proper sealing | Valve gate condition verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Valve Failure | Isolate water mist system sections for maintenance, testing, and controlled water release | ELP - External leakage - process medium | 2.4 Wear | Worn packing/stem seal leaks water externally | Valve packing condition and adjustment verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Valve Failure | Isolate water mist system sections for maintenance, testing, and controlled water release | ELP - External leakage - process medium | 2.2 Corrosion | Valve body corrosion pit penetrates wall | Valve body free of corrosion damage? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Valve Failure | Isolate water mist system sections for maintenance, testing, and controlled water release | ELP - External leakage - process medium | 1.4 Deformation | Flange gasket failure causes joint leak at valve | Valve flange bolts torque verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Valve Failure | Isolate water mist system sections for maintenance, testing, and controlled water release | PDE - Parameter deviation | 2.3 Erosion | Eroded valve trim alters flow characteristics | Valve Cv performance verified? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Valve Failure | Isolate water mist system sections for maintenance, testing, and controlled water release | PDE - Parameter deviation | 2.4 Wear | Worn internal parts allow internal bypass flow | Valve internal condition verified by inspection? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Valve Failure | Isolate water mist system sections for maintenance, testing, and controlled water release | PDE - Parameter deviation | 5.2 Contamination | Debris accumulation partially blocks valve flow path | Valve internals clean and free of debris? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Valve Failure | Isolate water mist system sections for maintenance, testing, and controlled water release | NOI - Noise | 2.1 Cavitation | Flashing across partially open valve creates noise | Valve pressure ratio within design limits? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Valve Failure | Isolate water mist system sections for maintenance, testing, and controlled water release | NOI - Noise | 2.3 Erosion | Eroded trim creates turbulence noise | Valve trim condition verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Valve Failure | Isolate water mist system sections for maintenance, testing, and controlled water release | NOI - Noise | 1.6 Sticking | Valve stem sticking creates intermittent chatter noise | Valve stem movement consistent during operation? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Power Supply Failure | Deliver uninterrupted electrical power to water mist pump motor and control systems | FTS - Failure to start on demand | 4.2 Open circuit | Circuit breaker tripped open prevents power delivery to system | Circuit breaker closed and latched? [Y/N] | TBD | Failure-Finding
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Power Supply Failure | Deliver uninterrupted electrical power to water mist pump motor and control systems | FTS - Failure to start on demand | 4.3 No power/voltage | Loss of main or backup power supply to fire system | Power supply availability verified? [Y/N] | TBD | Failure-Finding
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Power Supply Failure | Deliver uninterrupted electrical power to water mist pump motor and control systems | FTS - Failure to start on demand | 1.5 Looseness | Loose electrical connection at terminal interrupts power path | Electrical terminal connections torque verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Power Supply Failure | Deliver uninterrupted electrical power to water mist pump motor and control systems | NOO - No output | 4.3 No power/voltage | Power supply output zero due to internal converter failure | Power supply output voltage confirmed? [Y/N] | TBD | Failure-Finding
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Power Supply Failure | Deliver uninterrupted electrical power to water mist pump motor and control systems | NOO - No output | 2.5 Breakage | Blown fuse results in no output power to loads | Fuses intact and proper rating confirmed? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Power Supply Failure | Deliver uninterrupted electrical power to water mist pump motor and control systems | NOO - No output | 4.1 Short circuiting | Internal short circuit collapses output voltage | Power supply insulation resistance within limits? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Power Supply Failure | Deliver uninterrupted electrical power to water mist pump motor and control systems | FOV - Faulty output voltage | 4.4 Faulty power/voltage | Voltage regulator malfunction causes incorrect output voltage | Power supply output voltage within specified range? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Power Supply Failure | Deliver uninterrupted electrical power to water mist pump motor and control systems | FOV - Faulty output voltage | 3.4 Out of adjustment | Power supply calibration drifts from setpoint | Power supply calibration verified? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Power Supply Failure | Deliver uninterrupted electrical power to water mist pump motor and control systems | FOV - Faulty output voltage | 4.1 Short circuiting | Partial short circuit causes voltage deviation from nominal | Power supply output ripple measured? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Power Supply Failure | Deliver uninterrupted electrical power to water mist pump motor and control systems | OHE - Overheating | 5.1 Blockage/plugged | Cooling fan inlet blocked reduces heat dissipation from power supply | Power supply cooling fan operational? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Power Supply Failure | Deliver uninterrupted electrical power to water mist pump motor and control systems | OHE - Overheating | 5.2 Contamination | Dust accumulation on heatsink reduces cooling efficiency | Power supply heatsink clean and unobstructed? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Power Supply Failure | Deliver uninterrupted electrical power to water mist pump motor and control systems | OHE - Overheating | 4.1 Short circuiting | Internal partial short generates excess heat in power supply | Thermal protection device functional? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Power Supply Failure | Deliver uninterrupted electrical power to water mist pump motor and control systems | CSF - Control/signal failure | 3.4 Out of adjustment | Power supply control logic drifts affecting remote monitoring | Power supply status signals correct? [Y/N] | TBD | Predictive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Power Supply Failure | Deliver uninterrupted electrical power to water mist pump motor and control systems | CSF - Control/signal failure | 4.2 Open circuit | Communication wire break prevents remote status monitoring | Remote monitoring communication link functional? [Y/N] | TBD | Failure-Finding
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Power Supply Failure | Deliver uninterrupted electrical power to water mist pump motor and control systems | CSF - Control/signal failure | 3.3 Faulty signal/indication/alarm | Power supply status indicator shows incorrect state | Status indicator condition verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Alarm Device Failure * | Provide audible and visual alert of water mist system activation, abnormal condition, or system fault | CSF - Control/signal failure | 3.2 No signal/indication/alarm | Communication link loss prevents alarm activation | Alarm communication link functional? [Y/N] | TBD | Failure-Finding
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Alarm Device Failure * | Provide audible and visual alert of water mist system activation, abnormal condition, or system fault | CSF - Control/signal failure | 4.2 Open circuit | Broken alarm wiring interrupts signal path to annunciator | Alarm wiring continuity verified? [Y/N] | TBD | Preventive
SEWM - Fire Fighting System, Water Mist | Generate and distribute fine water mist to suppress fires by cooling, oxygen displacement, and radiant heat attenuation | Alarm Device Failure * | Provide audible and visual alert of water mist system activation, abnormal condition, or system fault | CSF - Control/signal failure | 3.4 Out of adjustment | Alarm threshold misconfigured in PLC prevents normal alarm | Alarm threshold settings confirmed